Release Notes V4.4

07 11 26 cs

Copyright SSAB Oxelösund AB 2007

Permission is granted to copy, distribute and/or modify this document
      under the terms of the GNU Free Documentation License, Version 1.2
      or any later version published by the Free Software Foundation;
      with no Invariant Sections, no Front-Cover Texts, and no Back-Cover Texts.

# Upgrading to Proview V4.4.0
This document describes new functions i Proview V4.4.0, and how to upgrade a project from V4.3.0 to V4.4.0.

# New functions
## OPC XML/DA Server
An OPC XML/DA Server is a web service from which an OPC XML/DA Client can get information of a Proview system. A opc client can, for example, browse the object hierachy, read and write attribute value, and subscribe to attributes.
The opc server implements the http protocol as well and is not connected to a web server. The port number of the opc_server is set to 80, the URI for the web service is on node 'mynode' is
http://mynode
If a web server is present, this normally has allocated the port 80, and another port has to be choosen for the opc_sever. If port 8080 is choosen, the URI will be
http://mynode:8080
#### Browsing
The OPC XML/DA browsing supports branches and items. The item contains a value, while the branch is an hierarchical component without a value. There is no support for objects, so an object has to be implemented as a branch, while an attribute is implemented as an item. Also arrays are implemented as branches, while array elements (that is not a class) is implemented as an item.
#### Threads
If the opc client uses the HoldTime and WaitTime attributes in the SubscriptionPolledRefresh request, the opc server has to be multi threaded, that is, for every request, an new thread is created. If the HoldTime and WaitTime is not used (as in the proview opc client), all requests can be handled in a single thread, which is less time consuming. Multithreads or not is configured in the configuration object for the opc server. The default value is 'IfNeeded' which turns on the multithreading for a client if HoldTime or WaitTime are detected.
#### Client access
To gain access to a proview opc server, the ip address of the client has to be configured in the configuration object for the opc server. Here you can also choose if the client has ReadWrite or ReadOnly access, where ReadOnly, allows the client to read and subscribe to attribute values, while ReadWrite also is allowed to write attribute values.

#### Buffering of subscriptions
The server does not support buffering of subscriptions.
### Configuration
The opc server is configured with a Opc_ServerConfig object that is placed under in the Node hierarchy. The configuration object will cause a server process (opc_server) to start at proview startup.
## OPC XML/DA Client
The proview opc client is implemented as an extern volume, which is mounted somewhere in the objects tree of the root volume. Under the mount object, the branches and items of the server are displayed with special opc objects. An Opc_Hier object represents a branch and Opc_Int an item with an integer value, Opc_Boolean an item with a boolean value etc. If an item object is opened the item value are displayed in a Value attribute, and some other properties as description, lowEU, highEU, engineeringUnit, lowIR and highIR are displayed. When the object is opened a subscription is started, and the value is continuously updated. For integer and float items there is also an object graph that displays a trend of the value.
With the opc client you can
- browse the branches and items in Xtt, and also display item values and set item values.
- subscribe item values and display them in a Ge graph.
- fetch item values into the plc logic and also write values to items.
The opc client requires that name browsing is implemented in the opc server.
### Ge
An item value can be displayed in a Ge graph by using the name in the extern volume. For example, if the mount object for the extern volume is 'Ext-P1', and the local name of the item is
 /P1/Signals/Ai22
the signal name in Ge will probably be (this is dependent of the browsing function of the server)
Ext-P1-P1-Signals-Ai22.Value##Float32
presuming that it is a float datatype.
### Plc
Item values can also be handled in the plc program, using the GetExt... and CStoExt... objects. The normally used objects for getting and storing attributes GetDp, GetAp, StoDp, StoAp etc. can not be used, as they require that the referenced name is known in the development environment, which is not the case for mosts extern volumes. In the Ext objects, the reference is made with a name string, making it possible to enter the item name. To get the value of the item in the previous example, you should use a GetExtFloat32 object, and the object name should be
Ext-P1-P1-Signals-Ai22.Value
To store a value in an item, lets say /P1/Signals/Ao5, you use a CstoExtFoat32. This objects makes a conditional storage, and only on a positive edge of the condition. Compare with the CstoAp, where the value is stored, as long as the condition is true. The reference name in the CstoExtFloat32 object in this case should be
Ext-P1-P1-Signals-Ao5.Value
### Client process
For each opc client-server connection a client process has to be started. The executable for this process i opc_provider that has the arguments
1. Opc server URL.
2. Extern volume id.
3. Extern volume name.
4. Server identity (optional, default 200).
### Configuration
#### Register ExternVolume
Register the externvolume in the GlobalVolumeList with a volume name and identity.
#### Application file
Add a line in the application file to start the opc_provider. Here is an example for a opc client connting to the opc server 'http://servernode:8080'. The registered externvolume has the name MyOpcVolume with volume id 0.1.99.55
opc_provider, opc_provider, noload, run, opc_provider, 9, nodebug, http://servernode:8080 0.1.99.55 MyOpcVolume
If item values are fetched into the plc, the priority should be set to 4 (sixth argument).
#### Mount object
Create a mount object in the plant hierarchy of the rootvolume. and insert the objid of the volumeobject in the externvolume into the Object attribute. In the example above this objid is _O0.1.99.55:0.
#### Hint
The application file reside on $pwrp_load and has the name $pwrp_load/ld_appl_'nodename'_'busnumber'.txt where node name is the name of the node, and busnumber the qcom bus number. If the node is 'mynode' and the busnumber is 507, the filename will be
 $pwrp_load/ls_appl_mynode_507.txt
## New functions in Ge
### Invisible
Dynamic type Invisible can be connected to analog values. When the value is zero, the object is made invisible.
### DigColor
Dynamic type DigColor can be connected to a bit in a bitmask. The type specification of the attribute should be ##Bit['bitnumber'], where bitnumber for the first bit is 0.
# New ClassVolume
## Opc
The Opc class volume contains classes for the opc client and server.
# New Types
### Int64
A base type for a 64 bit signed integer.
### UInt64
A base type for a 64 bit unsigned integer.
# New Classes
### Opc:Opc_ServerConfig
Configuration object for an opc server.
### Opc:Opc_ServerState
An object created as first object in the extern volume in an opc client, displaying information about the connected opc server.
### Opc:Opc_Hier
An object in the extern volume in an opc client representing a branch.
### Opc:Opc_String
An object in the extern volume in an opc client representing an item of datatype string.
### Opc:Opc_Boolean
An object in the extern volume in an opc client representing an item of datatype boolean.
### Opc:Opc_Float
An object in the extern volume in an opc client representing an item of datatype float.
### Opc:Opc_Double
An object in the extern volume in an opc client representing an item of datatype double.
### Opc:Opc_Decimal
An object in the extern volume in an opc client representing an item of datatype decimal.
### Opc:Opc_Long
An object in the extern volume in an opc client representing an item of datatype long.
### Opc:Opc_Int
An object in the extern volume in an opc client representing an item of datatype int.
### Opc:Opc_Short
An object in the extern volume in an opc client representing an item of datatype short.
### Opc:Opc_Byte
An object in the extern volume in an opc client representing an item of datatype byte.
### Opc:Opc_UnsignedLong
An object in the extern volume in an opc client representing an item of datatype unsignedLong.
### Opc:Opc_UnsignedInt
An object in the extern volume in an opc client representing an item of datatype unsignedInt.
### Opc:Opc_UnsignedShort
An object in the extern volume in an opc client representing an item of datatype unsignedShort.
### Opc:Opc_UnsignedByte
An object in the extern volume in an opc client representing an item of datatype unsignedByte.
### Opc:Opc_Base64Unary
An object in the extern volume in an opc client representing an item of datatype base64Unary.
### Opc:Opc_DateTime
An object in the extern volume in an opc client representing an item of datatype dateTime.
### Opc:Opc_Date
An object in the extern volume in an opc client representing an item of datatype date.
### Opc:Opc_Duration
An object in the extern volume in an opc client representing an item of datatype duration.
### Opc:Opc_QName
An object in the extern volume in an opc client representing an item of datatype QName.
### pwrb:GetExtBoolean
A plc object to fetch an attribute value of type Boolean from an extern volume.
### pwrb:GetExtFloat32
A plc object to fetch an attribute value of type Float32 from an extern volume.
### pwrb:GetExtFloat64
A plc object to fetch an attribute value of type Float64 from an extern volume.
### pwrb:GetExtInt8
A plc object to fetch an attribute value of type Int8 from an extern volume.
### pwrb:GetExtInt16
A plc object to fetch an attribute value of type Int16 from an extern volume.
### pwrb:GetExtInt32
A plc object to fetch an attribute value of type Int32 from an extern volume.
### pwrb:GetExtInt64
A plc object to fetch an attribute value of type Int64 from an extern volume.
### pwrb:GetExtUInt8
A plc object to fetch an attribute value of type UInt8 from an extern volume.
### pwrb:GetExtUInt16
A plc object to fetch an attribute value of type UInt16 from an extern volume.
### pwrb:GetExtUInt32
A plc object to fetch an attribute value of type UInt32 from an extern volume.
### pwrb:GetExtUInt64
A plc object to fetch an attribute value of type UInt64 from an extern volume.
### pwrb:GetExtString
A plc object to fetch an attribute value of type String from an extern volume.
### pwrb:GetExtTime
A plc object to fetch an attribute value of type Time from an extern volume.
### pwrb:CStoExtBoolean
A plc object for conditinal storage of a Boolean value into an attribute in an extern volume.
### pwrb:CStoExtFloat32
A plc object for conditinal storage of a Float32 value into an attribute in an extern volume.
### pwrb:CStoExtFloat64
A plc object for conditinal storage of a Float64 value into an attribute in an extern volume.
### pwrb:CStoExtInt8
A plc object for conditinal storage of a Int8 value into an attribute in an extern volume.
### pwrb:CStoExtInt16
A plc object for conditinal storage of a Int16 value into an attribute in an extern volume.
### pwrb:CStoExtInt32
A plc object for conditinal storage of a Int32 value into an attribute in an extern volume.
### pwrb:CStoExtInt64
A plc object for conditinal storage of a Int64 value into an attribute in an extern volume.
### pwrb:CStoExtUInt8
A plc object for conditinal storage of a UInt8 value into an attribute in an extern volume.
### pwrb:CStoExtUInt16
A plc object for conditinal storage of a UInt16 value into an attribute in an extern volume.
### pwrb:CStoExtUInt32
A plc object for conditinal storage of a UInt32 value into an attribute in an extern volume.
### pwrb:CStoExtUInt64
A plc object for conditinal storage of a UInt64 value into an attribute in an extern volume.
### pwrb:CStoExtString
A plc object for conditinal storage of a String value into an attribute in an extern volume.
### pwrb:CStoExtTime
A plc object for conditinal storage of a Time value into an attribute in an extern volume.
### pwrb:AtoFloat64
A plc object to convert a Float32 value to Float64.
### pwrb:Float64toA
A plc object to convert a Float64 value to Float32.
### pwrb:Int64toI
A plc object to convert a Int64 value to Int32.
### pwrb:ItoInt64
A plc object to convert a Int32 value to Int64.
### pwrb:UInt64toI
A plc object to convert a UInt64 value to Int32.
### pwrb:ItoUInt64
A plc object to convert a Int32 value to UInt64.
### pwrb:UInt32toI
A plc object to convert a UInt32 value to Int32.
### pwrb:ItoUInt32
A plc object to convert a Int32 value to Uint32.
# V4.4.1 additions
## Status Server
The Status Server is a server process that implements a web service that responds to a number of request to get status information about a process or operator station, and to start xtt on the current display. The Status Server has to be started if the Runtime Monitor or the Supervision Center is used (see below).
The Status Server (rt_statussrv) is started if a StatusServerConfig object is placed in the node hierarchy under the $Node object.
## Runtime Monitor
The runtime monitor starts, stops and monitors the runtime environment started on a development station. It is opened from the menu in the navigator Tools/Runtime Montor.

The runtime environment is started with the pushbutton Start Runtime and stopped with the pushbutton Stop Runtime. A soft restart is executed by the pushbutton Restart Runtime. File/Reset in the menu removes the runtime processes and shared memory, this sometimes has to be done, when the runtime environment is not correctly started or terminated. The current runtime status is displayed by the colored rectangle to the left, and in the lower part of the window. Xtt with or without operator window can be started from the menu or from buttons in the tools panel.
## Supervision Center
From the Supervision Center, a number of process and operator stations can be supervised. The system status for the station are fetched via the status monitor, that has to be started in the supervised nodes. New nodes are added by File/Add Node or the + button in the tools panel. For each node, the Description of the $Node object, the SystemStatus, SystemTime, BootTime, RestartTime, number of restarts and proview version are displayed. The SystemStatus can be opened, and then, the status of each system process add application process are displayed.
It is also possible to start xtt, with or without an operator window from the menu (File/Open Runtime Navigator and File/Open Operatorplace). To open an operator place, a valid OpPlace object has to be supplied when the node is added.
All changes of system status are stored in an eventlist, and by activating View/Pop Events the eventlist is popped on top of the screen when an error status is received.
The current configuration of process and operator stations are stored with File/Save Configuration.

## New classes
### pwrb:StatusServerConfig
Object to start the Status Server. Should be placed in the node hierarchy under the $Node object.
# V4.4.2 Additions
## New classes
### bcomp:BaseCDamper
Base object for a control damper.
### bcomp:BaseMDamper
Base object for a solenid damper.
### bcomp:BaseC3WayValve
Base object for a three way control valve.
### bcomp:BaseM3WayValve
Base object for a three way solenoid valve.
### bcomp:BaseFilter
Base object for a filter.
## Subgraphs
### Ventilation
Graphic symbols according to standard SS 03 22 60.
### Ventilation/Cooling
Graphic symbols according to standard SIS 03 22 31.
## Ge
Help for subgraphs added in help menu.
A popup menu with help entry added to subgraph palette to give help for a specific subgraph.
## Documentation
### Graphic Symbol Library
Documentaion about all Proview subgraphs. Available i xtthelp, pdf and html.
# V4.4.4 Additions
## New ClassVolume
### OtherIO
ClassVolume intended to contain small I/O systems.
## New Classes
### pwrs:$ClassLost
New systemclass to replace a lost class, for example when an object tree containg local classes are copied from another project.
### pwrb:BwInv
Plc object for bitwise invert.
### pwrb:BwRotateLeft
Plc object for bitwise left rotation.
### pwrb:BwRotateRight
Plc object for bitwise right rotation.
### pwrb:BwShiftLeft
Plc object for bitwise shift left.
### pwrb:BwShiftRight
Plc object for bitwise shift right.
### pwrb:Demux
Plc object for analog demultiplexer.
### pwrb:IDemux
Plc object for integer demultiplexer.
### pwrb:IpDistribute
Plc object to expand the number of integer ouputs handled in a DataArithm object.
### pwrb:IpCollect
Plc object to expand the number of integer inputs handled in a DataArithm object.
### pwrb:XyCurve
Object to store and display a curve of points with x,y coordinates.
### OtherManufacturer:Eurotherm_TC3001
Object for a Eurotherm TC3001 thyristor unit. New classes related to this class are also Eurotherm_TC3001Fo, Eurotherm_TC3001Sim, Eurotherm_TC3001_PbSlave, Eurotherm_TC3001_PbModule, Eurotherm_TC3001Aggr, Eurotherm, Eurotherm_TC3001AggrFo and Eurotherm_TC3001_AggrSim.
### OtherIO:MotionControl_USB
Rack object for a Motion Control USB I/O.
### OtherIO:MotionControl_USBIO
Card object for a Motion Control USB I/O.
## USB I/O
A new I/O device, Motion Control USB I/O, is attached to Proview. The device is connected to the USB port, and contains 21 channels with Di, Do, Ao and/or Ai. The device is configured with the classes OtherIO:MotionControl_USB and OtherIO:MotionControl_USBIO.
## Plc documentation on PDF
A plc window can be printed as PDF from File/Print/To Pdf File in the plc editor menu.
## XY Curve
New graphic component in Ge to draw a curve of points with x,y coordinates. The component is found under Analog in the Ge palette.
# Upgrade procedure
The upgrading has to be done from V4.3.0. If the project has a lower version, the upgrade has to be performed stepwise following the schema
V2.1 -> V2.7b -> V3.3 -> V3.4b -> V4.0.0 -> V4.1.3 -> V4.2.0 ->V4.4.0/V4.4.1/V4.4.2/V4.4.4
The upgrade procedure is to change the version of the project in the projectlist, and then activate Functions/Update Classes from the meny in the Configurator. If the V4.3 version should be kept, first make a copy of the project.

## Make a copy of the project
Do sdf to the project and start the administrator
> pwra
Now the Projectlist is opened. Enter edit mode, login as administrator if you lack access. Fined the current project and select Copy Project from the popup menu of the ProjectReg object. Open the copy and assign a suitable project name and path. Change the version to V4.4.0/V4.4.1. Save and close the administrator.
## Update Classes
Do sdf to the project.
Start the Configurator, enter edit mode, and activate Functions/Update Classes in the menu.
Save and Build.